Chapter 10, Solution 8C.

Heat rejected decreases; everything else increases.

Chapter 10, Solution 9C.

Heat rejected decreases; everything else increases.

Chapter 10, Solution 10C.

The pump work remains the same, the moisture content decreases, everything else increases.

Chapter 10, Solution 16.

A steam power plant that operates on a simple ideal Rankine cycle is considered. The quality of the steam at the turbine exit, the thermal efficiency of the cycle, and the mass flow rate of the steam are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis (a)  From the steam tables (Tables A-4, A-5, and A-6),

qin

qout

10 kPa

1

3

2

4

10 MPa

s

T

h1=hf @ 10 kPa=191.81  kJ/kg1f @ 10 kPa3

P3=10  MPa  h3=3375.1  kJ/kgs3=6.5995  kJ/kg⋅KP4=10  kPa  x4=s4−sfsfg=6.5995−0.64927.4996=0.7934h4=hf+x4hfg=191.81+0.79342392.1=2089.7  kJ/kg

(b)	qin=h3−h2=3375.1−201.90=3173.2 kJ/kgqout=h4−h1=2089.7−191.81=1897.9 kJ/kgwnet=qin−qout=3173.2−1897.9=1275.4 kJ/kg

and

ηth=wnetqin=1275.4  kJ/kg3173.2  kJ/kg=40.2%

(c)	m=Wnetwnet=210,000  kJ/s1275.4  kJ/kg=164.7  kgs

Chapter 10, Solution 34.

A steam power plant that operates on a reheat Rankine cycle is considered. The quality (or temperature, if superheated) of the steam at the turbine exit, the thermal efficiency of the cycle, and the mass flow rate of the steam are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis (a)  From the steam tables (Tables A-4, A-5, and A-6),

1

5

2s

6s

s

T

3

4s

10 MPa

10 kPa

6

4

2

h1=hf @ 10 kPa=191.81 kJ/kgv1=vf @ 10 kPa=0.001010  m3/kgwp, in=v1P2−P1ηp

P3=10  MPa  h3=3375.1   kJ/kgs3=6.5995 kJ/kg⋅KP4s=1  MPa  h4s=2783.8 kJ/kg

P6s=10 kPa  x6s=s6s−sfsfg=7.7642−0.64927.4996=0.9487 at  turbine  exith6s=hf+x6shfg=191.81+0.94872392.1=2461.2  kJ/kgηT=h5−h6h5−h6s  h6h5−ηTh5−h6s3479.1−0.803479.1−2461.22664.8  kJ/kg > hg superheated vapor

From steam tables at 10 kPa we read  T6 = 88.1C.

(b)	wT,out=h3−h4+h5−h6=3375.1−2902.0+3479.1−2664.8=1287.4 kJ/kgqin=h3−h2+h5−h4=3375.1−202.43+3479.1−2902.0=3749.8 kJ/kg

Thus the thermal efficiency is

ηth=wnetqin=1276.8  kJ/kg3749.8  kJ/kg=34.1%

(c)  The mass flow rate of the steam is

m=Wnetwnet=80,000  kJ/s1276.9  kJ/kg=62.7  kg/s

Chapter 10, Solution 44.

A steam power plant that operates on an ideal regenerative Rankine cycle with an open feedwater heater is considered. The net work output per kg of steam and the thermal efficiency of the cycle are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis (a)  From the steam tables (Tables A-4, A-5, and A-6),

1

qin

2

7

s

T

5

6

6

MPa

20 kPa

0.4 MPa

1-y

4

y

3

qout

h1=hf @ 20 kPa=251.42   kJ/kgv1=vf @ 20 kPa=0.001017   m3/kg

P3=0.4 MPa  h3=hf @ 0.4 MPa=604.66 kJ/kgv3=vf @ 0.4 MPa=0.001084  m3/kgwpII, in=v3P4−P3 =0.001084   m3/kg6000−400   kPa1  kJ1  kPa⋅m3 =6.07   kJ/kg

The fraction of steam extracted is determined from the steady-flow energy balance equation applied to the feedwater heater. Noting that Q≃W≃Δke≃Δpe≃0,

Ein−Eout=ΔEsystemÃ0(steady)=0Ein=Eoutmihi=mehe  m6h6+m2h2=m3h3  yh6+1−yh2=1h3

where y is the fraction of steam extracted from the turbine (=m6m3).  Solving for y,

y=h3−h2h6−h2=604.66−251.812665.7−251.81=0.1462

Then,

qin=h5−h4=3302.9−610.73=2692.2  kJ/kgqout=1−yh7−h1=1−0.14622214.0−251.42=1675.7 kJ/kg

And	wnet=qin−qout=2692.2−1675.7=1016.5  kJ/kg

(b) The thermal efficiency is determined from

ηth=1−qoutqin=1−1675.7  kJ/kg2692.2  kJ/kg=37.8%

Chapter 10, Solution 49.

A steam power plant operates on an ideal reheat-regenerative Rankine cycle with an open feedwater heater. The mass flow rate of steam through the boiler and the thermal efficiency of the cycle are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

1

2

8

s

T

5

7

0.8 MPa

10 kPa

y

4

3

6

1 - y

10 MPa

Analysis (a)  From the steam tables (Tables A-4, A-5, and A-6),

h1=hf @ 10 kPa=191.81 kJ/kg1f @ 10 kPa3pI, in1P2−P10.00101   m3/kg800−10  kPa1  kJ1  kPa⋅m3

y

5

8

1

2

3

4

Turbine

Boiler

Condenser

Open

fwh

P I

P II

6

7

1-y

6

P3=0.8 MPa  h3=hf @ 0.8 MPa=720.87 kJ/kgv3=vf @ 0.8 MPa=0.001115   m3/kgpII, in3P4−P30.001115   m3/kg10,000−800  kPa1  kJ1  kPa⋅m3

The fraction of steam extracted is determined from the steady-flow energy balance equation applied to the feedwater heaters. Noting that Q≃W≃Δke≃Δpe≃0,

Ein−Eout=ΔEsystemÃ0(steady)=0  →   {Ein=Eoutmihi=mehe  m6h6+m2h2=m3h3  yh6+1−yh2=1h3

where y is the fraction of steam extracted from the turbine ().  Solving for y,

y=h3−h2h6−h2=720.87−192.612812.1−192.61=0.2017

Then,   qin=h5−h4+1−yh7−h6=3502.0−731.12+1−0.20173481.3−2812.1=3305.1  kJ/kgqout=1−yh8−h1=1−0.20172494.7−191.81=1838.5  kJ/kgwnet=qin−qout=3305.1−1838.5=1466.6 kJ/kg

and 	m=Wnetwnet=80,000  kJ/s1466.1  kJ/kg=54.5  kg/s

(b)	ηth=wnetqin=1466.1  kJ/kg3305.1  kJ/kg=44.4%

Chapter 10, Solution 50.

A steam power plant operates on an ideal reheat-regenerative Rankine cycle with a closed feedwater heater. The mass flow rate of steam through the boiler and the thermal efficiency of the cycle are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis

1

2

8

s

T

5

7

0.8 MPa

10 kPa

y

4

3

6

1 - y

10 MPa

9

10

6

5

8

1

2

3

4

Turbine

Boiler

Condenser

Closed

fwh

P I

P II

y

7

1-y

Mixing

chamber

10

9

(a)  From the steam tables (Tables A-4, A-5, and A-6),

h1=hf @ 10 kPa=191.81 kJ/kgv1=vf @ 10 kPa=0.00101 m3/kgpI, inv1P2−P1=0.00101   m3/kg10,000−10  kPa1  kJ1  kPa⋅m3

Also, h4 = h9 = h10 = 731.12 kJ/kg  since the two fluid streams that are being mixed have the same enthalpy.

P5=10 MPa  h5=3502.0 kJ/kgs5=6.7585  kJ/kg⋅KP6=0.8  MPa  h6=2812.7 kJ/kgP7=0.8  MPa  h7=3481.3  kJ/kgs7=7.8692  kJ/kg⋅KP8=10 kPa x8=s8−sfsfg=7.8692−0.64927.4996=0.9627h8=hf+x8hfg=191.81+0.96272392.1=2494.7  kJ/kg

The fraction of steam extracted is determined from the steady-flow energy balance equation applied to the feedwater heaters. Noting that Q≃W≃Δke≃Δpe≃0,

Ein−Eout=ΔEsystemÃ0(steady)=0Ein=Eoutmihi=mehe  m2h9−h2=m3h6−h3  1−yh9−h2=yh6−h3

where y is the fraction of steam extracted from the turbine ().  Solving for y,

y=h9−h2h6−h3+h9−h2=731.13−201.902812.7−720.87+731.13−201.90=0.2019

Then,

qin=h5−h4+1−yh7−h6=3502.0−731.13+1−0.20193481.3−2812.7=3304.5 kJ/kgqout=1−yh8−h1=1−0.20192494.7−191.81=1837.9 kJ/kgwnet=qin−qout=3304.5−1837.8=1466.6 kJ/kg

and

m=Wnetwnet=80,000  kJ/s1467.1  kJ/kg=54.5  kg/s

(b)	ηth=1−qoutqin=1−1837.8  kJ/kg3304.5  kJ/kg=44.4%

Chapter 10, Solution 68E.

A large food-processing plant requires steam at a relatively high pressure, which is extracted from the turbine of a cogeneration plant. The rate of heat transfer to the boiler and the power output of the cogeneration plant are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis

(a)  From the steam tables (Tables A-4E, A-5E, and A-6E),

6

8

1

5

Turbine

Boiler

Condenser

Process

heater

P I

P II

4

2

3

7

h1=hf  @  2  psia=94.02  Btu/lbm1f @ 2 psia3

Mixing chamber:

1

2

8

s

T

6

7s

1000 psia

2 psia

80 psia

4

5

3

Qin

·

Qprocess

·

7

8s

or,

h4=m2h2+m3h3m4=394.29+2282.135=169.43 Btu/lbm4f @ hf=169.43 Btu/lbm3

66

7s7s6 7s

Then, 	Qin=m5h6−h5=5  lbm/s1506.2−172.72 Btu/lbm=6667  Btu/s

(b)	WT,out=ηTWT, s=ηTm6h6−h7s+m8h7s−h8s0.86