ME 470 Vapor and Combined Power Cycles Hw Solutions   Inst:  Shoeleh Di Julio

Chapter 10, Solution 22.

A steam power plant operates on a simple ideal Rankine cycle between the specified pressure limits. The thermal efficiency of the cycle, the mass flow rate of the steam, and the temperature rise of the cooling water are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis (a)  From the steam tables (Tables A-4, A-5, and A-6),

qin

qout

10 kPa

1

3

2

4

7 MPa

s

T

h1=hf @ 10 kPa=191.81  kJ/kg1f @ 10 kPa3wp, in=v1P2−P1=0.00101   m3/kg7,000−10  kPa1  kJ1  kPa⋅m37.06  kJ/kg2

P3=7 MPa  h3=3411.4  kJ/kgs3=6.8000 kJ/kg⋅KP4=10 kPa  x4=s4−sfsfg=6.8000−0.64927.4996=0.8201h4=hf+x4hfg=191.81+0.82012392.1=2153.6  kJ/kg

Thus,	qin=h3−h2=3411.4−198.87=3212.5 kJ/kgqout=h4−h1=2153.6−191.81=1961.8 kJ/kgwnet=qin−qout=3212.5−1961.8=1250.7 kJ/kg

and	ηth=wnetqin=1250.7  kJ/kg3212.5  kJ/kg=38.9%

(b)	m=Wnetwnet=45,000  kJ/s1250.7  kJ/kg=36.0  kgs

(c)  The rate of heat rejection to the cooling water and its temperature rise are

Qout=mqout=35.98  kg/s1961.8  kJ/kg=70,586   kJ/sΔTcooling water=Qout(mc)cooling water=70,586  kJ/s2000 kg/s4.18  kJ/kg⋅°C=8.4°C

Chapter 10, Solution 49.

A steam power plant operates on an ideal reheat-regenerative Rankine cycle with an open feedwater heater. The mass flow rate of steam through the boiler and the thermal efficiency of the cycle are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

1

2

8

s

T

5

7

0.8 MPa

10 kPa

y

4

3

6

1 - y

10 MPa

Analysis (a)  From the steam tables (Tables A-4, A-5, and A-6),

h1=hf @ 10 kPa=191.81 kJ/kg1f @ 10 kPa3pI, in1P2−P10.00101   m3/kg800−10  kPa1  kJ1  kPa⋅m3

y

5

8

1

2

3

4

Turbine

Boiler

Condenser

Open

fwh

P I

P II

6

7

1-y

6

P3=0.8 MPa  h3=hf @ 0.8 MPa=720.87 kJ/kgv3=vf @ 0.8 MPa=0.001115   m3/kgpII, in3P4−P30.001115   m3/kg10,000−800  kPa1  kJ1  kPa⋅m3

The fraction of steam extracted is determined from the steady-flow energy balance equation applied to the feedwater heaters. Noting that Q≃W≃Δke≃Δpe≃0,

Ein−Eout=ΔEsystemÃ0(steady)=0  →   {Ein=Eoutmihi=mehe  m6h6+m2h2=m3h3  yh6+1−yh2=1h3

where y is the fraction of steam extracted from the turbine ().  Solving for y,

y=h3−h2h6−h2=720.87−192.612812.1−192.61=0.2017

Then,   qin=h5−h4+1−yh7−h6=3502.0−731.12+1−0.20173481.3−2812.1=3305.1  kJ/kgqout=1−yh8−h1=1−0.20172494.7−191.81=1838.5  kJ/kgwnet=qin−qout=3305.1−1838.5=1466.6 kJ/kg

and 	m=Wnetwnet=80,000  kJ/s1466.1  kJ/kg=54.5  kg/s

(b)	ηth=wnetqin=1466.1  kJ/kg3305.1  kJ/kg=44.4%

Chapter 10, Solution 50.

A steam power plant operates on an ideal reheat-regenerative Rankine cycle with a closed feedwater heater. The mass flow rate of steam through the boiler and the thermal efficiency of the cycle are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis

1

2

8

s

T

5

7

0.8 MPa

10 kPa

y

4

3

6

1 - y

10 MPa

9

10

6

5

8

1

2

3

4

Turbine

Boiler

Condenser

Closed

fwh

P I

P II

y

7

1-y

Mixing

chamber

10

9

(a)  From the steam tables (Tables A-4, A-5, and A-6),

h1=hf @ 10 kPa=191.81 kJ/kgv1=vf @ 10 kPa=0.00101 m3/kgpI, inv1P2−P1=0.00101   m3/kg10,000−10  kPa1  kJ1  kPa⋅m3

Also, h4 = h9 = h10 = 731.12 kJ/kg  since the two fluid streams that are being mixed have the same enthalpy.

P5=10 MPa  h5=3502.0 kJ/kgs5=6.7585  kJ/kg⋅KP6=0.8  MPa  h6=2812.7 kJ/kgP7=0.8  MPa  h7=3481.3  kJ/kgs7=7.8692  kJ/kg⋅KP8=10 kPa x8=s8−sfsfg=7.8692−0.64927.4996=0.9627h8=hf+x8hfg=191.81+0.96272392.1=2494.7  kJ/kg

The fraction of steam extracted is determined from the steady-flow energy balance equation applied to the feedwater heaters. Noting that Q≃W≃Δke≃Δpe≃0,

Ein−Eout=ΔEsystemÃ0(steady)=0Ein=Eoutmihi=mehe  m2h9−h2=m3h6−h3  1−yh9−h2=yh6−h3

where y is the fraction of steam extracted from the turbine ().  Solving for y,

y=h9−h2h6−h3+h9−h2=731.13−201.902812.7−720.87+731.13−201.90=0.2019

Then,

qin=h5−h4+1−yh7−h6=3502.0−731.13+1−0.20193481.3−2812.7=3304.5 kJ/kgqout=1−yh8−h1=1−0.20192494.7−191.81=1837.9 kJ/kgwnet=qin−qout=3304.5−1837.8=1466.6 kJ/kg

and

m=Wnetwnet=80,000  kJ/s1467.1  kJ/kg=54.5  kg/s

(b)	ηth=1−qoutqin=1−1837.8  kJ/kg3304.5  kJ/kg=44.4%

Chapter 10, Solution 67.

A cogeneration plant is to generate power and process heat. Part of the steam extracted from the turbine at a relatively high pressure is used for process heating. The net power produced and the utilization factor of the plant are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

Analysis  From the steam tables (Tables A-4, A-5, and A-6),

6

8

1

5

Turbine

Boiler

Condenser

Process

heater

P I

P II

4

2

3

7

h1=hf @  10  kPa=191.81  kJ/kg1f  @  10  kPa3

Mixing chamber:

Ein−Eout=ΔEsystemä0(steady)=0Ein=Eoutmihi=mehe  m4h4=m2h2+m3h3

1

2

8

s

T

6

7

7 MPa

10 kPa

0.6 MPa

4

5

3

Qout

·

Qin

·

Qprocess

·

or,	h4=m2h2+m3h3m4=22.50192.41+7.50670.3830=311.90  kJ/kg4f @ hf=311.90  kJ/kg3

66

776 h7=2774.6 kJ/kg

Then,

WT,out=m6h6−h7+m8h7−h830 kg/s3411.4−2774.622.5  kg/s

Also,	Qprocess=m7h7−h3=7.5  kg/s2774.6−670.38 kJ/kg=15,782 kW

and	Qin=m5h6−h5=30  kg/s3411.4−318.47=92,788  kW

Chapter 10, Solution 70.

A cogeneration plant modified with regeneration is to generate power and process heat. The mass flow rate of steam through the boiler for a net power output of 15 MW is to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible.

6

8

1

5

Turbine

Boiler

Condenser

Process

heater

P I

P II

9

2

3

7

4

fwh

Analysis

From the steam tables (Tables A-4, A-5, and A-6),

1

2

8

s

T

6

7

6 MPa

10 kPa

0.4 MPa

5

3,4,9

h1=hf @ 10  kPa=191.81 kJ/kg1f  @  10  kPa3

66 66

Then, per kg of steam flowing through the boiler, we have

wT,out=h6−h7+0.4h7−h83302.9−2665.70.4

wp, in=0.4wpI, in+wpII, in0.40.39  kJ/kg

Thus,

m=Wnetwnet=15,000  kJ/s845.8  kJ/kg=17.73  kg/s

Chapter 10, Solution 76.

A combined gas-steam power cycle is considered. The topping cycle is a gas-turbine cycle and the bottoming cycle is a simple ideal Rankine cycle. The mass flow rate of the steam, the net power output, and the thermal efficiency of the combined cycle are to be determined.

Assumptions 1 Steady operating conditions exist. 2 Kinetic and potential energy changes are negligible. 3 Air is an ideal gas with constant specific heats.

Properties The properties of air at room temperature are cp = 1.005 kJ/kg·K and k = 1.4 (Table A-2).

1

2

4

s

T

3

10 MPa

15 kPa

6

Qout

·

Qin

·

5

9

8

7

GAS

CYCLE

STEAM

CYCLE

1500 K

300 K

400C

420 K

Analysis (a)  The analysis of gas cycle yields

T6=T5P6P5k−1k=300  K160.41.4=662.5  KQin=mairh7−h6=maircpT7−T6

From the steam tables (Tables A-4, A-5, and A-6),

h1=hf @ 15 kPa=225.94 kJ/kg1f @ 15 kPa3

P3=10 MPa 3h3=3097.0 kJ/kg3

Noting thatQ≃W≃Δke≃Δpe≃0for the heat exchanger, the steady-flow energy balance equation yields

Ein−Eout=ΔEsystemÃ0(steady)=0Ein=Eoutmihi=mehe  msh3−h2=mairh8−h9ms=h8−h9h3−h2mair=cpT8−T9h3−h2mair=1.005  kJ/kg⋅K679.3−420  K3097.0−236.06  kJ/kg14  kg/s=1.275   kg/s

(b)	WT,steam=msh3−h4=1.275  kg/s3097.0−2011.5  kJ/kg=1384  kWWp, steam=mswp=1.275  kg/s10.12  kJ/kg=12.9 kWWnet, steam=WT, steam−Wp, steam=1384−12.9=1371 kW

and	Wnet=Wnet, steam+Wnet, gas=1371+6448=7819  kW

(c)	ηth=WnetQin=7819  kW11,784  kW=66.4%